## Answer key
Clause | Requirement (as the specification states it) | Spec page | ABC Switchgear Pvt Ltd |  |  |  | XYZ Electricals Ltd |  |  |  | PQR Power Systems
|  |  | Correct result | Evidence document | Page | Why | Correct result | Evidence document | Page | Why | Correct result | Evidence document | Page | Why
2.1 | The bidder shall have designed, manufactured and supplied not less than 200 numbers of 11kV Vacuum Circuit Breakers to any State Electricity Board or Distribution Licensee in India during the last five years. | 2 | Complied | ABC_credentials.pdf | 1 | [OCR] 340 numbers supplied to MSEDCL, against a floor of 200 | Complied | XYZ_credentials.pdf | 1 | 410 numbers | Complied | PQR_credentials.pdf | 1 | [OCR] 260 numbers, above the floor of 200 -- legible despite a poor photocopy
2.2 | The bidder shall have an average annual turnover of not less than Rs. 10 crore during the last three financial years. | 2 | Complied | ABC_audited_balance_sheets.pdf | 1 | Rs. 42.6 crore average, against a floor of Rs. 10 crore; the credentials state the same figure | Complied | XYZ_audited_balance_sheets.pdf | 1 | Rs. 18.2 crore average | Not Complied | PQR_credentials.pdf | 1 | [TRAP OCR] Rs. 6.4 crore against a floor of Rs. 10 crore. Read 6.4 as 64 and a bidder below the floor clears it by a factor of ten.
2.3 | The bidder shall own and operate an in-house routine testing facility at the manufacturing works, and shall furnish photographic evidence and a list of test equipment with valid calibration certificates. | 2 | Complied | ABC_test_equipment_list_and_calibration_certificates.pdf | 1 | facility at Nashik, with a calibrated equipment list | Complied | XYZ_test_equipment_list_and_calibration_certificates.pdf | 1 | facility at Vadodara, with a calibrated equipment list | Needs Human Review | — | — | [TRAP] nothing in the bundle mentions a testing facility either way. No facility evidence was submitted. Must NOT be guessed in either direction.
2.4 | The bidder shall not have been blacklisted or debarred by any utility in India during the last three years, and shall furnish a self-declaration to that effect on company letterhead. | 3 | Complied | ABC_self_declaration.pdf | 1 | declaration of no blacklisting, on letterhead | Complied | XYZ_self_declaration.pdf | 1 | declaration of no blacklisting | Complied | PQR_self_declaration.pdf | 1 | declaration of no blacklisting
3.1 | The circuit breaker shall conform in all respects to IS 13118 and IEC 62271-100, and to the latest amendments thereof. | 4 | Complied | ABC_guaranteed_technical_particulars.pdf | 1 | GTP cites IS 13118 and IEC 62271-100; the type test report agrees | Complied | XYZ_guaranteed_technical_particulars.pdf | 1 | GTP cites both standards | Not Complied | PQR_guaranteed_technical_particulars.pdf | 1 | [TRAP OCR] the GTP cites IS 13118 only. IEC 62271-100 is required as well and appears nowhere in the bundle. A present standard makes this read as compliant unless both are checked.
3.2 | The operating mechanism shall be of the motor wound spring charged type, suitable for both local and remote operation. | 4 | Complied | ABC_guaranteed_technical_particulars.pdf | 1 | motor wound spring charged | Complied | XYZ_guaranteed_technical_particulars.pdf | 1 | motor wound spring charged | Complied | PQR_guaranteed_technical_particulars.pdf | 1 | [OCR] motor wound spring charged
3.3 | All type test reports submitted shall be not older than five years from the date of bid opening. | 4 | Complied | ABC_type_test_report.pdf | 1 | report dated 08-09-2023, inside the five-year window | Complied | XYZ_type_test_report.pdf | 1 | report dated 22-02-2024, inside the window; NABL valid to 30-06-2027 | Complied | PQR_type_test_report.pdf | 1 | [OCR] the report is dated 14-11-2023, which IS inside the five-year window. The lapsed accreditation is a separate failure, recorded against mandatory document (d) -- this row is about the report's age and nothing else.
3.4 | The following type tests shall have been carried out on the offered equipment: short circuit breaking current test, lightning impulse withstand test, power frequency withstand test and temperature rise test. | 4 | Complied | ABC_type_test_report.pdf | 1 | all four named tests carried out and PASSED | Complied | XYZ_type_test_report.pdf | 1 | all four named tests PASSED | Not Complied | PQR_type_test_report.pdf | 1 | [TRAP OCR] three of the four named tests are reported. The power frequency withstand test is absent.
3.4 T1 | Rated voltage shall be 11 kV. | 5 | Complied | ABC_guaranteed_technical_particulars.pdf | 1 | [OCR] 11 kV | Complied | XYZ_guaranteed_technical_particulars.pdf | 1 | 11 kV | Complied | PQR_guaranteed_technical_particulars.pdf | 1 | [OCR] 11 kV, on the worst scan in the set
3.4 T2 | Rated short circuit breaking current shall be 25 kA for 3 seconds. | 5 | Complied | ABC_guaranteed_technical_particulars.pdf | 1 | [OCR] 25 kA for 3 seconds | Not Complied | XYZ_deviation_sheet.pdf | 1 | [TRAP] 20 kA offered against 25 kA required. The DECLARED deviation, stated on the Deviation Sheet and visible in the GTP. | Not Complied | PQR_guaranteed_technical_particulars.pdf | 1 | [TRAP OCR] 25 kA for 1 second. The CURRENT matches the requirement and the DURATION does not. The hardest row in the key, and the Deviation Sheet says NIL, so the bidder contradicts itself.
3.4 T3 | Rated frequency shall be 50 Hz. | 5 | Complied | ABC_guaranteed_technical_particulars.pdf | 1 | [OCR] 50 Hz | Complied | XYZ_guaranteed_technical_particulars.pdf | 1 | 50 Hz | Complied | PQR_guaranteed_technical_particulars.pdf | 1 | [OCR] 50 Hz
3.4 T4 | Degree of protection of the enclosure shall be IP 4X or better. | 5 | Complied | ABC_guaranteed_technical_particulars.pdf | 1 | [OCR] IP 4X, exactly the minimum | Not Complied | XYZ_guaranteed_technical_particulars.pdf | 1 | [TRAP] IP 2X is WORSE than the required IP 4X, and is NOT declared on the Deviation Sheet. Reads as a match to anything not comparing the digit. | Complied | PQR_guaranteed_technical_particulars.pdf | 1 | [OCR] IP 55 exceeds the required IP 4X. Requires understanding that a higher rating satisfies a minimum.
3.4 T5 | Auxiliary supply voltage shall be 110 V DC. | 5 | Complied | ABC_guaranteed_technical_particulars.pdf | 1 | [OCR] 110 V DC | Not Complied | XYZ_guaranteed_technical_particulars.pdf | 1 | [TRAP] 110 V AC against 110 V DC required, and NOT declared. One letter apart, a different thing entirely. | Needs Human Review | — | — | [TRAP] the GTP has no auxiliary supply row at all. No evidence means no verdict -- never a pass, and never a failure either.
4.1 | Routine tests shall be carried out on each circuit breaker in the presence of the purchaser's representative, and test certificates shall be submitted for approval before despatch. | 6 | Complied | ABC_quality_assurance_plan.pdf | 1 | QAP commits to routine tests before the purchaser's representative | Complied | XYZ_quality_assurance_plan.pdf | 1 | QAP commits to it | Needs Human Review | — | — | [TRAP] no Quality Assurance Plan was submitted, so nothing commits to the routine-test regime. The Technical Offer's blanket claim of compliance is not evidence of a test procedure.
4.2 | The bidder shall submit a Quality Assurance Plan for approval within fifteen days of the date of the purchase order. | 6 | Complied | ABC_quality_assurance_plan.pdf | 1 | a QAP was submitted with the offer | Complied | XYZ_quality_assurance_plan.pdf | 1 | a QAP was submitted | Not Complied | — | — | [TRAP RULE] the clause requires a Quality Assurance Plan to be submitted, and none was. Suggested by the rule, then confirmed by the engineer -- never decided by the classifier alone.
4.3 | Any equipment failing a routine test shall be replaced at the bidder's cost. | 6 | Complied | ABC_quality_assurance_plan.pdf | 1 | failing equipment replaced at the bidder's cost | Complied | XYZ_quality_assurance_plan.pdf | 1 | replaced at our cost | Needs Human Review | — | — | nothing in the bundle undertakes to replace failed equipment at the bidder's cost.
5.1 | The equipment shall be guaranteed against defective design, material and workmanship for a period of 18 months from the date of commissioning or 24 months from the date of despatch, whichever is earlier. | 7 | Complied | ABC_performance_bank_guarantee_undertaking.pdf | 1 | 18 months from commissioning or 24 from despatch, as the clause words it | Complied | XYZ_performance_bank_guarantee_undertaking.pdf | 1 | 18 / 24 months as worded | Needs Human Review | — | — | no guarantee undertaking was submitted.
5.2 | The bidder shall furnish a performance bank guarantee for 10 percent of the order value, valid for the full guarantee period. | 7 | Complied | ABC_performance_bank_guarantee_undertaking.pdf | 1 | performance bank guarantee, 10 percent, full guarantee period | Complied | XYZ_performance_bank_guarantee_undertaking.pdf | 1 | 10 percent for the full guarantee period | Needs Human Review | — | — | no performance bank guarantee undertaking was submitted.

## Mandatory documents
Item | Mandatory document | Bidder | Correct result | Document submitted | Why
a) | Technical Offer, being this specification signed and stamped | ABC Switchgear Pvt Ltd | Complied | ABC_technical_offer.pdf | signed and stamped
a) | Technical Offer, being this specification signed and stamped | XYZ Electricals Ltd | Complied | XYZ_technical_offer.pdf | signed and stamped
a) | Technical Offer, being this specification signed and stamped | PQR Power Systems | Complied | PQR_technical_offer.pdf | signed and stamped
b) | Deviation Sheet | ABC Switchgear Pvt Ltd | Complied | ABC_deviation_sheet.pdf | says NIL, the only compliant form of this document
b) | Deviation Sheet | XYZ Electricals Ltd | Not Complied | XYZ_deviation_sheet.pdf | [TRAP] the sheet lists a deviation, so it is not NIL. This is the defect that defines bidder 2.
b) | Deviation Sheet | PQR Power Systems | Complied | PQR_deviation_sheet.pdf | says NIL, so the document itself is compliant -- while the GTP offers 1 second against 3 seconds required. The contradiction is the finding, not this row.
c) | Guaranteed Technical Particulars | ABC Switchgear Pvt Ltd | Complied | ABC_guaranteed_technical_particulars.pdf | submitted
c) | Guaranteed Technical Particulars | XYZ Electricals Ltd | Complied | XYZ_guaranteed_technical_particulars.pdf | submitted
c) | Guaranteed Technical Particulars | PQR Power Systems | Complied | PQR_guaranteed_technical_particulars.pdf | submitted
d) | Type test reports from a NABL accredited laboratory | ABC Switchgear Pvt Ltd | Complied | ABC_type_test_report.pdf | CPRI report, NABL certificate TC-7741 valid at the bid date
d) | Type test reports from a NABL accredited laboratory | XYZ Electricals Ltd | Complied | XYZ_type_test_report.pdf | ERDA report, NABL certificate TC-5588 valid to 30-06-2027
d) | Type test reports from a NABL accredited laboratory | PQR Power Systems | Not Complied | PQR_type_test_report.pdf | [TRAP] the report is present, but the laboratory's NABL accreditation TC-6612 expired 31-03-2024, before the bid. An accreditation that has lapsed is not an accreditation. Anything that does not check the date passes this.
e) | Audited balance sheets for the last three financial years | ABC Switchgear Pvt Ltd | Complied | ABC_audited_balance_sheets.pdf | three financial years, certified
e) | Audited balance sheets for the last three financial years | XYZ Electricals Ltd | Complied | XYZ_audited_balance_sheets.pdf | three financial years, certified
e) | Audited balance sheets for the last three financial years | PQR Power Systems | Not Complied | NOT SUBMITTED | [TRAP] audited balance sheets were never submitted. THE MISSING MANDATORY DOCUMENT that defines bidder 3.

## Expected outcome
Bidder | What this bidder is for | Correct technical status | Because
ABC Switchgear Pvt Ltd | everything correct — measures false alarms | Qualified | every requirement and every mandatory document complied.
XYZ Electricals Ltd | Deviation Sheet is not NIL (one declared deviation, two undeclared) | Not Qualified | 4 Not Complied: requirement 3.4 T2, requirement 3.4 T4, requirement 3.4 T5, document b). Any single Not Complied means Not Qualified.
PQR Power Systems | missing mandatory document, expired NABL accreditation, worst scans, no QAP | Not Qualified | 7 Not Complied: requirement 2.2, requirement 3.1, requirement 3.4, requirement 3.4 T2, requirement 4.2, document d), document e). Any single Not Complied means Not Qualified.

## Read me
TBE Workbench — POC answer key
Data set version 1.0. Generated, not hand-edited.
What this is
The correct result for every requirement and every bidder, used to measure whether the platform is right. We have no BSES documents yet, so the specification and the three bidder bundles are synthetic: we planted the problems, so we know the answers.
How it was produced
eval/poc/requirements.py holds the requirement list, read out of the specification PDF and checked back against it.
eval/poc/bundles.py builds the three bidder bundles as image-only scans, with signatures and stamps over the text.
eval/poc/answer_key.py holds this key and refuses to run if it cites a clause the specification does not contain or a document the bundle does not hold.
Rebuild everything with: .venv\Scripts\python.exe make_test_data.py
The counts
18 requirements (4 qualification) x 3 bidders = 54 rows, plus 5 mandatory documents x 3 = 15 rows.
10 rows are marked TRAP: a wrong 'Complied' there is silent and dangerous.
16 rows are marked OCR: the answer sits on a degraded scan.
1 requirement rows are marked RULE: decided by Python in tbe/rules.py or tbe/validity.py, not by the model. All mandatory-document rows are RULE rows.
How to read a result
TBE is pass/fail. There is no score and no ranking. Any single requirement or mandatory document confirmed Not Complied means the bidder is Not Qualified — a bidder at 95% compliance is not better than one at 70%, both are out.
A row with no evidence is 'Needs Human Review', never 'Complied'. A bidder with any unresolved row cannot be Qualified yet.
Caution
These documents are deliberately nastier than a real bundle in places and certainly gentler in others. Figures measured against them describe our system, not a promise about BSES paperwork. Replace all of it when the client's real specification, bundle and past completed TBE arrive.